## Room Data
Standard Components - Room Data Sheet
Date of issue: 28.06.2021
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
CTPR | CT Planning Room | 45 | 8am to 6pm, Monday – Friday (extended hours, weekends and/or emergency access may be required) | 1 patient; up to 3 staff assisting |  | Acoustic privacy is required | The CT Planning Room provides space and facilities for Computed Tomography (CT) scanning procedures as part of the planning of radiation therapy treatment for patients. A collocated Control Room with observation window is required for the remote operation of equipment. An Equipment Room may be required and will need to be in close proximity due to acceptable cable lengths. Cable ducts between the Scanning Room, Control Room and Equipment Room will be required. Equipment is to be installed to manufacturer's specifications with sufficient clearances for maintenance access. The CT Planning Room must be adequately shielded. Radiation shielding is to be as advised and confirmed by a Radiation Consultant to suit the equipment procured. 'X-ray in Use' lights are required outside each entry door to be illuminated when scanning begins. Interlock system to doors recommended to prevent machine from running if door open and to stop the machine upon entry if in use. Additional Considerations: Additional medical gases may be provided (including additional oxygen, additional suction, nitrous oxide and scavenge) depending on clinical requirements, such as the provision of anaesthetic services. Dimmable lights are to be provided and lights are to be placed to avoid glare to patients. Back lit ceiling artwork may be installed for patient comfort and distraction. Where possible, it is preferred that ductwork in the ceiling is designed to the perimeter of room to allow for future flexibility to provide ceiling mounted equipment. The need for and extent of emergency and UPS power must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. Unistrut ceiling able to carry moving loads may be required. A mix of respiratory gating, surface guidance, motion management and/or patient position technologies may be provided depending on clinical/service requirements and will be coordinated to support the technologies provided in the Linear Accelerator Treatment Room. The provision of these technologies is to be confirmed by the project and may have additional design requirements including additional power/data, water cooling, heat load, possible increased set down, increased number of trenches/conduits, space requirements for computer cabinets in control room and additional penetrations through the suspended ceiling. Requirements to be confirmed with vendors.

## Items
Standard Components - Items in room
Date of issue: 28.06.2021
Generated by dRofus (C) dRofus
Items
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment
CTPR | CT Planning Room | FA | FLVY-001 | FLOOR FINISH: vinyl, seamless, coved, anti-static | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
CTPR | CT Planning Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 10
CTPR | CT Planning Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 3
CTPR | CT Planning Room | FA | WLWA-007 | WALL FINISH: splashback | 1
CTPR | CT Planning Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 5
CTPR | CT Planning Room | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 7
CTPR | CT Planning Room | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
CTPR | CT Planning Room | FA | DWOB-009 | OBSERVATION: internal window, lead glass, clear | 1 | safety glass, to control room
CTPR | CT Planning Room | FA | DWSC-005 | DOOR: 910mm c/o, single leaf, solid core, lead shielding, paint | 1 | to control room
CTPR | CT Planning Room | FA | DWSC-034 | DOOR: 1800mm c/o, double leaf, solid core, lead shielding, paint | 1
CTPR | CT Planning Room | FA | CLCN-009 | CORNICE: wall trim fixing | 1
CTPR | CT Planning Room | FFE | FIHR-019 | BRACKET: for suction bottle | 1
CTPR | CT Planning Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
CTPR | CT Planning Room | FFE | FIJO-135 | CUPBOARD: underbench, double door, adj shelves | 3
CTPR | CT Planning Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
CTPR | CT Planning Room | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
CTPR | CT Planning Room | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
CTPR | CT Planning Room | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
CTPR | CT Planning Room | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
CTPR | CT Planning Room | FFE | FIHR-030 | HOOK: equipment, on mounting plate | 1 | for patient slide
CTPR | CT Planning Room | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1
CTPR | CT Planning Room | FFE | MGFP-004 | FLOWMETER: oxygen | 1
CTPR | CT Planning Room | FFE | MMBE-042 | SLIDE: patient | 1 | patient transfer devices to be based on operational requirements and WHS policies
CTPR | CT Planning Room | FFE | MMGE-139 | TROLLEY: procedure | 1
CTPR | CT Planning Room | FFE | MMGE-142 | TROLLEY: sharps bin | 1
CTPR | CT Planning Room | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 2
CTPR | CT Planning Room | FFE | MMGE-002 | ADAPTER: suction | 1
CTPR | CT Planning Room | FFE | MMGE-100 | SUCTION BOTTLE | 1
CTPR | CT Planning Room | FFE | FQCW-005 | BIN: waste, clinical, 20L | 1
CTPR | CT Planning Room | FFE | HYBA-010 | BASIN: handwash, Type B | 1
CTPR | CT Planning Room | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
CTPR | CT Planning Room | FFE | ITCL-012 | CAMERA: observation | 2 | 1 x optional, for patient observation or visualisation of additional monitoring equipment, pan, tilt and zoom (PTZ) capability is required, quantity to be based on equipment and service requirements
CTPR | CT Planning Room | FFE | ITCL-014 | CLOCK: analogue, electric | 1
CTPR | CT Planning Room | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1
CTPR | CT Planning Room | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1
CTPR | CT Planning Room | FFE | MMMI-105 | TABLE: patient, fixed, CT | 1
CTPR | CT Planning Room | FFE | MMMI-107 | INJECTOR: contrast, CT, ceiling mounted | 1 | may be mobile
CTPR | CT Planning Room | FFE | MMMI-109 | DEVICE: imaging, CT, wide bore | 1
CTPR | CT Planning Room | FFE | FIJO-166 | CUPBOARD: tall, shelving, horizontal patient device storage, radiotherapy | 2
CTPR | CT Planning Room | FFE | FIJO-167 | CUPBOARD: tall, shelving, vertical patient device storage, radiotherapy | 1
CTPR | CT Planning Room | FFE | FIJO-212 | BULKHEAD: joinery | 2 | plasterboard bulkhead is also acceptable
CTPR | CT Planning Room | FFE | MMMI-377 | WARMER: contrast | 1 | may be located in control room
CTPR | CT Planning Room | FFE | FIHR-077 | BRACKET: for observation camera, ceiling mounted | 1
CTPR | CT Planning Room | FFE | FIHR-078 | BRACKET: for observation camera, wall mounted | 1
CTPR | CT Planning Room | FFE | MMRA-008 | DEVICE: surface guided radiation therapy system | 1 | as required for respiratory gating / motion management / surface guidance systems, to suit service requirements
CTPR | CT Planning Room | FFE | MMRA-014 | LASER: radiotherapy, bridge | 1 | wall and ceiling mounted lasers are also acceptable
CTPR | CT Planning Room | FFE | MMRA-020 | OVEN: thermoplastic warming | 1
CTPR | CT Planning Room | FFE | FIHR-092 | HOOK: anchor, patient ladder | 1
CTPR | CT Planning Room | FFE | MMRA-019 | LASER: radiotherapy, couch tracking | 1
CTPR | CT Planning Room | FFE | FIHR-089 | BRACKET: surface guided radiation therapy system, ceiling mounted | 1
CTPR | CT Planning Room | SE | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 2 | 1 x optional, to additional patient observation camera if provided
CTPR | CT Planning Room | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1
CTPR | CT Planning Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
CTPR | CT Planning Room | SE | ELPR-006 | RCD: residual current device | 3
CTPR | CT Planning Room | SE | ELGP-101 | GPO: single, ceiling mounted | 2 | 1 x optional, to additional patient observation camera if provided
CTPR | CT Planning Room | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1
CTPR | CT Planning Room | SE | ELBO-001 | BUTTON: emergency stop | 1
CTPR | CT Planning Room | SE | LIFX-002 | LIGHT: illuminated sign, "X-Ray in Use" | 2 | outside room doors, auto-on when modality in use
CTPR | CT Planning Room | SE | ELBO-015 | SWITCH: light, single | 1
CTPR | CT Planning Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
CTPR | CT Planning Room | SE | MGAS-062 | OUTLET: suction, on services panel | 1
CTPR | CT Planning Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 1
CTPR | CT Planning Room | SE | ELGP-109 | GPO: single, wall mounted | 2 | to clock
CTPR | CT Planning Room | SE | ELGP-208 | GPO: double, wall mounted | 4
CTPR | CT Planning Room | SE | ITSE-025 | DOOR RELEASE: access control, remote activation | 1
CTPR | CT Planning Room | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
CTPR | CT Planning Room | SE | WLSH-004 | SHIELDING: lead lining | 1 | to walls and doors, shielding to be reviewed and confirmed by Radiation Consultant
CTPR | CT Planning Room | SE | ELBO-012 | SWITCH: light, dimmer | 1
CTPR | CT Planning Room | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
CTPR | CT Planning Room | SE | ELGP-122 | GPO: emergency power, single, on services panel | 3
CTPR | CT Planning Room | SE | LIFX-038 | LIGHT: backlit feature panels | 2 | desirable